## Guidance notes
Guidance notes for S-Plan wiring schemes applicable to Alpha CD-R series condensing boilers
1) | Electrical work must only be carried out by competent persons in accordance with the requirements of the current BS7671.
2) | Suitability of schematic for a specific installation must be checked prior to starting work since connections vary depending upon the components used.
All examples use my own preferred system components of Horstmann C27 controller, Danfoss-Randall TP5000 programmable room thermostat and
Honeywell L641A cylinder thermostat. These are chosen for reliability and functionality at a very economic cost compared to other options.
3) | Check terminal connections if different control components are used and update drawing accordingly. There is no defined 'standard' among manufacturers.
4) | Earth wires are not shown for clarity but all component earth wires must be connected to terminal 3.
5) | Wires only terminate in terminals. Similar colour wires crossing each other are shown as a dashed line.
6) | Wire colours shown improve clarity of the schematic but do not necessarily represent the actual wire colour used.
7) | It is recommended to update the drawing using the actual wire colours utilised in each specific system.
8) | For boiler connections, use 24/0.2 (0.75mm) flexible cables, 3-core for pump and 5-core for boiler.
9) | Use heatproof cable for connections to pumps, thermostats, boiler etc. where specified by the manufacturer.
10) | The Heat Dump relay, where used, must be installed in a suitable enclosure - it is normally easiest to include the main terminal connections in the same
housing. All cables entering and leaving the enclosure must be suitably glanded or enclosed within plastic trunking as necessary.
11) | Solar controller sensor terminals are isolated from the mains. Never connect anything other than a sensor wire to these terminals.
12) | The Alpha CD-R boilers are initially supplied with a wire link between boiler terminals 1 & 2. Remove this link at installation.
13) | Do NOT connect CH pump neutral or boiler PN terminals to the main incoming comon neutral supply wire.
14) | Ensure that solar controller Heat Dump cut-in temperature is below 90 degrees C to prevent over-temp tripping of boiler control electronics.
15) | Under the new IEE wiring regulations for fixed wiring (mandatory from April 2006):
|  | became | for Twin + E
|  | became | for Triple + E

## Solar S-Plan HD bypass Sorel
S-Plan (2-Zone) Fully Pumped Wiring Scheme with Solar System, Sorel Solar Controller and Bypass Heat Dump
Use this version ONLY if a single radiator is permanently connected to the boiler pump circuit as a bypass e.g. bathroom radiator
* For Alpha CD-R series condensing boilers ONLY *
[6 empty] | HW |  | CH |  | HW |  | CH
[6 empty] | OFF |  | OFF |  | ON |  | ON |  |  |  |  | COM | ON |  | OFF | [23 empty] | S3 |  |  |  | S2 |  |  |  | S1
| Horstmann |  | N | L |  | 1 |  | 2 |  | 3 |  | 4 |  |  |  |  | C | 1 |  | 2 | Cylinder Stat | [16 empty] | Sorel TDC2 / TDC3
| C27 controller | [19 empty] | Honeywell L641A | [16 empty] | PT1000 sensor connections
[26 empty] | OFF | ON |  | COM | [14 empty] | Cyl top |  |  |  | Cyl lower |  |  |  | Collector
[22 empty] | Danfoss TP5000 |  |  |  | NC | NO |  | COM
Room stat
4PCO relay - ON with Controller R2 ('Heat Dump' mode)
[35 empty] | C1 9 | NO1 5 | NC1 1 |  | C2 10 | NO2 6 | NC2 2 | C3 11 | NO3 7 |  | NC3 3 |  | C4 12 |  | NO4 8 |  | NC4 4 |  | Coil 13 |  | Coil 14
230Vac feed from | [25 empty] | Alpha CD-R Boiler |  |  |  |  | N/C | N/C | N/C
DP Sw/Fused |  | 1 |  | 2 |  |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 | 9 |  | 10 | Connection Terminal Box |  |  | F2A fuse |  | L | N |  |  | 1 | 2 | 3 | 4 | PL | PN |  |  |  | N | L |  |  |  | R2 |  | N |  | L |  | N |  | R1 |  | N
spur with 3A fuse | [7 empty] | 3
CH Pump
Sorel TDC2/3
Controller
[13 empty] | Bl |  | Br |  | Or | Gy |  |  |  | Bl | Br |  | Or | Gy |  | 2 off 2-port Zone Valves | [23 empty] | L |  | N
e.g. Horstmann Z222XL
[14 empty] | ZV Central Heating | [8 empty] | ZV DHW |  |  |  |  | or Honeywell V4043H | [23 empty] | Solar Pump
Warning: Please read guidance notes accompanying this schematic before use
Suggested relays:
Finder type 5534-8230-0040 in DIN socket type 94.74SMA available from Farnell Components, stock codes 116-9224 (relay) and 913-7653 (DIN relay socket)
or
OMRON type MY4 220/240ACS in DIN socket type PYF14AE also available from Farnell Components, stock codes 186-508 (relay) and 134-0953 (socket). Optional retaining clips 103-923 (2 off required)
Caution: Use of alternative relay may require pin number changes.
In the above schematic:
Relay contact 1 applies a direct Live feed to the CH (boiler) pump in HD mode.
Relay contact 2 inhibits boiler SwL supply to prevent boiler firing in HD mode.
Relay contact 3 opens DHW zone valve in HD mode.
Relay contact 4 is not used but allows future expansion to full CH HD if bypass radiator is insufficient. | [46 empty] | © A.J.Cooper June 2021

## Solar S-Plan HD bypass Resol
S-Plan (2-Zone) Fully Pumped Wiring Scheme with Solar System, Resol Solar Controller with Bypass Heat Dump
Use this version ONLY if a single radiator is permanently connected to the boiler pump circuit as a bypass e.g. bathroom radiator
* For Alpha CD-R series condensing boilers ONLY *
[5 empty] | HW |  | CH |  | HW |  | CH
[5 empty] | OFF |  | OFF |  | ON |  | ON |  |  |  |  | COM | ON | OFF | [23 empty] | S1 |  |  |  | S2 |  |  |  | S3 |  |  |  | S4
| Horstmann |  | N | L | 1 |  | 2 |  | 3 |  | 4 |  |  |  |  | C | 1 | 2 | Cylinder Stat | [14 empty] | Resol BS3 / BS4 | [7 empty] | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8
| C27 controller | [17 empty] | Honeywell L641A | [14 empty] | PT1000 sensor connections
[23 empty] | OFF |  | ON |  | COM | [14 empty] | Collector |  |  |  | Cyl lower |  |  |  | Cyl top |  |  |  | Return
[20 empty] | Danfoss TP5000 |  |  | NC |  | NO |  | COM | [26 empty] | (optional)
Room stat
4PCO relay - ON with Controller R2 ('Heat Dump' mode)
[35 empty] | C1 9 |  | NO1 5 |  | NC1 1 | C2 10 | NO2 6 |  | NC2 2 |  | C3 11 |  | NO3 7 |  | NC3 3 |  | C4 12 |  | NO4 8 |  | NC4 4 |  | Coil 13 |  | Coil 14
230Vac feed from | [13 empty] | N/C | [9 empty] | Alpha CD-R Boiler |  |  |  |  | N/C | N/C | N/C | [10 empty] | Earth |  | Earth |  | Earth | [5 empty] | N |  | R1 |  | N |  | L
DP Sw/Fused |  | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 | 9 | 10 | Connection Terminal Box |  |  | F2A fuse |  | L |  | N |  | 1 | 2 | 3 | 4 | PL | PN |  |  | N |  | L |  |  |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20
spur with 3A fuse | [6 empty] | 3
[36 empty] | CH Pump | [11 empty] | N |  | R2
Resol BS3 / BS4 Controller
[12 empty] | Bl |  | Br |  | Or | Gy |  |  | Bl | Br | Or | Gy |  |  | 2 off 2-port Zone Valves | [25 empty] | N |  | L
e.g. Horstmann Z222XL
[13 empty] | ZV Central Heating | [7 empty] | ZV DHW |  |  |  |  | or Honeywell V4043H | [25 empty] | Solar Pump
Warning: Please read guidance notes accompanying this schematic before use
Suggested relays:
Finder type 5534-8230-0040 in DIN socket type 94.74SMA available from Farnell Components, stock codes 116-9224 (relay) and 913-7653 (DIN relay socket)
or
OMRON type MY4 220/240ACS in DIN socket type PYF14AE also available from Farnell Components, stock codes 186-508 (relay) and 134-0953 (socket). Optional retaining clips 103-923 (2 off required)
Caution: Use of alternative relay may require pin number changes.
In the above schematic:
Relay contact 1 applies a direct Live feed to the CH (boiler) pump in HD mode.
Relay contact 2 inhibits boiler SwL supply to prevent boiler firing in HD mode.
Relay contact 3 opens DHW zone valve in HD mode.
Relay contact 4 is not used but allows future expansion to full CH HD if bypass radiator is insufficient. | [50 empty] | © A.J.Cooper July 2008

## Solar S-Plan HD to CH Sorel
S-Plan (2-Zone) Fully Pumped Wiring Scheme with Solar System, Sorel Solar Controller with Full Radiator Heat Dump
Use this version to dump excess heat into the entire central heating radiator circuit
* For Alpha CD-R series condensing boilers ONLY *
[5 empty] | HW |  | CH |  | HW |  | CH
[5 empty] | OFF |  | OFF |  | ON |  | ON |  |  |  |  | COM | ON |  | OFF | [21 empty] | S3 |  |  | S2 |  |  |  | S1
| Horstmann |  | N | L | 1 |  | 2 |  | 3 |  | 4 |  |  |  |  | C | 1 |  | 2 | Cylinder Stat | [14 empty] | Sorel TDC2 / TDC3
| C27 controller | [18 empty] | Honeywell L641A | [14 empty] | PT1000 sensor connections
[24 empty] | OFF |  | ON |  | COM | [12 empty] | Cyl top |  |  | Cyl lower |  |  |  | Collector
[21 empty] | Danfoss TP5000 |  |  | NC |  | NO |  | COM
Room stat
4PCO relay - ON with Controller R2 ('Heat Dump' mode)
[34 empty] | C1 9 |  | NO1 5 | NC1 1 | C2 10 | NO2 6 | NC2 2 |  | C3 11 | NO3 7 |  | NC3 3 |  | C4 12 |  | NO4 8 |  | NC4 4 |  | Coil 13 |  | Coil 14
230Vac feed from | [13 empty] | N/C | [10 empty] | Alpha CD-R Boiler |  |  |  |  | N/C | N/C | N/C
DP Sw/Fused |  | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 | 9 |  | 10 | Connection Terminal Box |  |  | F2A fuse |  | L |  | N |  | 1 | 2 | 3 | 4 | PL | PN |  |  |  | N | L |  |  |  |  | R2 |  | N |  | L |  | N |  | R1 |  | N
spur with 3A fuse | [6 empty] | 3
CH Pump
Sorel TDC2/3
Controller
[12 empty] | Bl |  | Br |  | Or | Gy |  |  |  | Bl | Br | Or | Gy |  |  | 2 off 2-port Zone Valves | [24 empty] | L |  | N
e.g. Horstmann Z222XL
[13 empty] | ZV Central Heating | [8 empty] | ZV DHW |  |  |  |  | or Honeywell V4043H | [24 empty] | Solar Pump
Warning: Please read guidance notes accompanying this schematic before use
Suggested relays:
Finder type 5534-8230-0040 in DIN socket type 94.74SMA available from Farnell Components, stock codes 116-9224 (relay) and 913-7653 (DIN relay socket)
or
OMRON type MY4 220/240ACS in DIN socket type PYF14AE also available from Farnell Components, stock codes 186-508 (relay) and 134-0953 (socket). Optional retaining clips 103-923 (2 off required)
Caution: Use of alternative relay may require pin number changes.
In the above schematic:
Relay contact 1 applies a direct Live feed to the CH (boiler) pump in HD mode.
Relay contact 2 inhibits boiler SwL supply to prevent boiler firing in HD mode.
Relay contact 3 opens DHW zone valve in HD mode.
Relay contact 4 opens CH zone valve in HD mode. | [45 empty] | © A.J.Cooper June 2021

## Solar S-Plan HD to CH Resol
S-Plan (2-Zone) Fully Pumped Wiring Scheme with Solar System, Resol Solar Controller with Full Radiator Heat Dump
Use this version to dump excess heat into the entire central heating radiator circuit
* For Alpha CD-R series condensing boilers ONLY *
[5 empty] | HW |  | CH |  | HW |  | CH
[5 empty] | OFF |  | OFF |  | ON |  | ON |  |  |  |  | COM | ON | OFF | [23 empty] | S1 |  |  |  | S2 |  |  |  | S3 |  |  |  | S4
| Horstmann |  | N | L | 1 |  | 2 |  | 3 |  | 4 |  |  |  |  | C | 1 | 2 | Cylinder Stat | [14 empty] | Resol BS3 / BS4 | [7 empty] | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8
| C27 controller | [17 empty] | Honeywell L641A | [14 empty] | PT1000 sensor connections
[23 empty] | OFF |  | ON |  | COM | [14 empty] | Collector |  |  |  | Cyl lower |  |  |  | Cyl top |  |  |  | Return
[20 empty] | Danfoss TP5000 |  |  | NC |  | NO |  | COM | [26 empty] | (optional)
Room stat
4PCO relay - ON with Controller R2 ('Heat Dump' mode)
[35 empty] | C1 9 | NO1 5 |  | NC1 1 |  | C2 10 | NO2 6 |  | NC2 2 |  | C3 11 |  | NO3 7 |  | NC3 3 |  | C4 12 |  | NO4 8 |  | NC4 4 |  | Coil 13 | Coil 14
230Vac feed from | [13 empty] | N/C | [9 empty] | Alpha CD-R Boiler |  |  |  |  | N/C | N/C | N/C | [11 empty] | Earth |  | Earth |  | Earth | [5 empty] | N |  | R1 |  | N | L
DP Sw/Fused |  | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 | 9 | 10 | Connection Terminal Box |  |  | F2A fuse |  | L |  | N |  | 1 | 2 | 3 | 4 | PL | PN |  |  |  | N |  | L |  |  |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 | 20
spur with 3A fuse | [6 empty] | 3
[37 empty] | CH Pump | [11 empty] | N |  | R2
Resol BS3 / BS4 Controller
[12 empty] | Bl |  | Br |  | Or | Gy |  |  | Bl | Br | Or | Gy |  |  | 2 off 2-port Zone Valves | [26 empty] | N |  | L
e.g. Horstmann Z222XL
[13 empty] | ZV Central Heating | [7 empty] | ZV DHW |  |  |  |  | or Honeywell V4043H | [26 empty] | Solar Pump
Warning: Please read guidance notes accompanying this schematic before use
Suggested relays:
Finder type 5534-8230-0040 in DIN socket type 94.74SMA available from Farnell Components, stock codes 116-9224 (relay) and 913-7653 (DIN relay socket)
or
OMRON type MY4 220/240ACS in DIN socket type PYF14AE also available from Farnell Components, stock codes 186-508 (relay) and 134-0953 (socket). Optional retaining clips 103-923 (2 off required)
Caution: Use of alternative relay may require pin number changes.
In the above schematic:
Relay contact 1 applies a direct Live feed to the CH (boiler) pump in HD mode.
Relay contact 2 inhibits boiler SwL supply to prevent boiler firing in HD mode.
Relay contact 3 opens DHW zone valve in HD mode.
Relay contact 4 opens CH zone valve in HD mode.
© A.J.Cooper July 2008

## Standard S-Plan
Standard S-Plan (2-Zone) Fully Pumped Wiring Scheme
* For Alpha CD-R series condensing boilers ONLY *
[6 empty] | HW |  | CH |  | HW |  | CH
[6 empty] | OFF |  | OFF |  | ON |  | ON |  |  |  | COM |  | ON |  | OFF
| Horstmann |  | N | L |  | 1 |  | 2 |  | 3 |  | 4 |  |  |  | C |  | 1 |  | 2 |  | Cylinder Stat
| C27 controller | [20 empty] | Honeywell L641A
[22 empty] | OFF |  | ON |  | COM
[22 empty] | NC |  | NO |  | COM | Danfoss TP5000
Room Stat
[13 empty] | N/C | [15 empty] | N/C | N/C | N/C
230Vac feed from |  | 1 | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 | 8 | 9 | 10 |  |  |  | F2A fuse |  |  | L |  | N |  |  | 1 | 2 | 3 | 4 | PL | PN |  | N | L
DP Sw/Fused | [5 empty] | 3
spur with 3A fuse | [27 empty] | Alpha CD-R Boiler | [6 empty] | CH Pump
[7 empty] | Bl |  | Br |  | Or |  | Gy |  |  |  | Bl |  | Br |  | Or |  | Gy |  |  | 2 off 2-port Zone Valves
Horstmann Z222XL or
[8 empty] | ZV Central Heating | [10 empty] | ZV DHW | [6 empty] | Honeywell V4043H
[6 empty] | Warning: Please read guidance notes accompanying this schematic before use | [27 empty] | © A.J.Cooper July 2008