## Guidance notes
Guidance notes for S-Plan wiring schemes
1) | Electrical work must only be carried out by competent persons in accordance with the requirements of the current BS7671.
2) | Suitability of schematic for a specific installation must be checked prior to starting work since connections vary depending upon the components used.
All examples use my own preferred system components of Horstmann C27 controller, Danfoss-Randall TP5000 programmable room thermostat and
Honeywell L641A cylinder thermostat. These are chosen for reliability and functionality at a very economic cost compared to other options.
3) | Check terminal connections if different components are used and update drawing accordingly. There is no defined 'standard' among manufacturers.
4) | Earth wires are not shown for clarity but all component earth wires must be connected to terminal 3.
5) | Wires only terminate in terminals. Similar colour wires crossing each other are shown as a dashed line.
Wire colours shown improve clarity of the schematic but do not necessarily represent the actual wire colour used.
6) | It is recommended to update the drawing using the actual wire colours utilised in each specific system.
7) | For boiler wiring, either a 1mm Triple+E plus Twin+E is used and/or a 5-core 24/0.2 flexible cable as appropriate.
8) | Use heatproof cable for connections to pumps, thermostats, boiler etc. where specified by the manufacturer.
9) | Solar schematics with Heat Dump options are only suitable for boilers utilising common-neutrals to boiler and pump i.e. with a switched pump live.
10) | The Heat Dump relay, where used, must be installed in a suitable enclosure - it is normally easiest to include the main terminal connections in the same
housing. All cables entering and leaving the enclosure must be suitably glanded or enclosed within plastic trunking as necessary.
11) | Solar controller sensor terminals are isolated from the mains. Never connect anything other than a sensor wire to these terminals.
12) | Under the new IEE wiring regulations for fixed wiring (mandatory from April 2006):
|  | became | for Twin + E
|  | became | for Triple + E

## Solar S-Plan Std Sorel
S-Plan (2-Zone) Fully Pumped Wiring Scheme with Standard Solar System, Sorel Solar Controller
[5 empty] | HW |  | CH |  | HW |  | CH
[5 empty] | OFF |  | OFF |  | ON |  | ON |  |  |  | COM | ON | OFF | [11 empty] | S3 |  |  | S2 |  | S1
| Horstmann |  | N | L | 1 |  | 2 |  | 3 |  | 4 |  |  |  | C | 1 | 2 | Cylinder Stat
| C27 controller | [16 empty] | Honeywell L641A
[22 empty] | OFF | ON |  | COM |  |  |  | Cyl top |  |  | Cyl lower |  | Collector
[22 empty] | NC | NO |  | COM | Danfoss TP5000
[26 empty] | Room stat |  |  | Sorel TDC2 / TDC3 controller
PT1000 sensor connections
* See note
Sorel TDC2/3 Controller
230Vac feed from | [13 empty] | N/C
DP Sw/Fused |  | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 | 8 | 9 | 10 | Connection Terminal Box |  |  | N | L | SwL |  | PL | PN | N | L | R2 |  | N | L | N | R1 | N
spur with 3A fuse | [6 empty] | 3
[23 empty] | Boiler |  |  |  | Boiler Pump
[12 empty] | Bl |  | Br | Or | Gy |  |  | Bl | Br | Or | Gy |  | 2 off 2-port Zone Valves | [9 empty] | L | N
e.g. Horstmann Z222XL
[13 empty] | ZV Central Heating | [6 empty] | ZV DHW |  |  |  | or Honeywell V4043H | [9 empty] | Solar Pump
* Note: For boilers without a Pump Live (PL) terminal, connect the Boiler Pump live to Terminal 10 or Boiler 'SwL' terminal.
Warning: Please read guidance notes accompanying this schematic before use
© A.J.Cooper June 2021

## Solar S-Plan Std Resol
S-Plan (2-Zone) Fully Pumped Wiring Scheme with Standard Solar System, Resol Solar Controller
[5 empty] | HW |  | CH |  | HW |  | CH
[5 empty] | OFF |  | OFF |  | ON |  | ON |  |  |  | COM | ON | OFF | [12 empty] | S1 |  | S2 |  |  | S3 |  | S4
| Horstmann |  | N | L | 1 |  | 2 |  | 3 |  | 4 |  |  |  | C | 1 | 2 | Cylinder Stat | [11 empty] | 1 | 2 | 3 | 4 |  | 5 | 6 | 7 | 8
| C27 controller | [16 empty] | Honeywell L641A
[22 empty] | OFF | ON |  | COM |  |  |  |  | Collector |  | Cyl lower |  |  | Cyl top |  | Return
[19 empty] | Danfoss TP5000 |  |  | NC | NO |  | COM | [11 empty] | (optional)
[19 empty] | Room stat | [12 empty] | Resol BS3 / BS4 controller
PT1000 sensor connections
[24 empty] | * See note | [6 empty] | Resol BS3 / BS4 controller
230Vac feed from | [13 empty] | N/C | [14 empty] | Earth | Earth | Earth |  |  |  | N | R1 | N | L
DP Sw/Fused |  | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 | 8 | 9 | 10 | Connection Terminal Box |  |  | N | L | SwL |  | PL | PN | N | L | 12 | 13 | 14 | 15 | 16 |  | 17 | 18 | 19 | 20
spur with 3A fuse | [6 empty] | 3
[23 empty] | Boiler |  |  |  | Boiler Pump |  |  |  |  | N | R2
[12 empty] | Bl |  | Br | Or | Gy |  |  | Bl | Br | Or | Gy |  | 2 off 2-port Zone Valves | [10 empty] | N | L
e.g. Horstmann Z222XL
[13 empty] | ZV Central Heating | [6 empty] | ZV DHW |  |  |  | or Honeywell V4043H | [10 empty] | Solar Pump
* Note: For boilers without a Pump Live (PL) terminal, connect the Boiler Pump live to Terminal 10 or Boiler 'SwL' terminal.
Warning: Please read guidance notes accompanying this schematic before use
© A.J.Cooper June 2008

## Solar S-Plan HD bypass Sorel
S-Plan (2-Zone) Fully Pumped Wiring Scheme with Solar System, Sorel Solar Controller and Bypass Heat Dump
Use this version ONLY if a single radiator is permanently connected to the boiler pump circuit as a bypass e.g. bathroom radiator
[6 empty] | HW |  | CH |  | HW |  | CH
[6 empty] | OFF |  | OFF |  | ON |  | ON |  |  |  |  | COM | ON | OFF | [17 empty] | S3 |  |  | S2 |  |  |  | S1
| Horstmann |  | N | L |  | 1 |  | 2 |  | 3 |  | 4 |  |  |  |  | C | 1 | 2 | Cylinder Stat | [10 empty] | Sorel TDC2 / TDC3
| C27 controller | [18 empty] | Honeywell L641A | [10 empty] | PT1000 sensor connections
[24 empty] | OFF | ON |  | COM | [9 empty] | Cyl top |  |  | Cyl lower |  |  |  | Collector
[21 empty] | Danfoss TP5000 |  |  | NC | NO |  | COM
Room stat
4PCO relay - ON with Controller R2 ('Heat Dump' mode)
[30 empty] | C1 9 |  | NO1 5 | NC1 1 | C2 10 | NO2 6 | NC2 2 |  | C3 11 | NO3 7 |  | NC3 3 |  | C4 12 |  | NO4 8 |  | NC4 4 |  | Coil 13 |  | Coil 14
230Vac feed from | [14 empty] | N/C
DP Sw/Fused |  | 1 |  | 2 |  |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 | 9 | 10 | Connection Terminal Box |  |  | N | L | SwL |  | PL | PN | N | L | [9 empty] | R2 |  | N |  | L |  | N |  | R1 |  | N
spur with 3A fuse | [7 empty] | 3
[25 empty] | * Boiler |  |  |  | Boiler Pump
Sorel TDC2/3
Controller
[13 empty] | Bl |  | Br |  | Or | Gy |  |  | Bl | Br | Or | Gy |  | 2 off 2-port Zone Valves | [21 empty] | L |  | N
e.g. Horstmann Z222XL
[14 empty] | ZV Central Heating | [7 empty] | ZV DHW |  |  |  | or Honeywell V4043H | [21 empty] | Solar Pump
* For boilers without a PL terminal there will be no connection between Boiler 'PL' and relay 'NC1'. In this case simply link Relay terminal 'NC1' to Relay terminal 'C2'.
Warning: Please read guidance notes accompanying this schematic before use
Suggested relays:
Finder type 5534-8230-0040 in DIN socket type 94.74SMA available from Farnell Components, stock codes 116-9224 (relay) and 913-7653 (DIN relay socket)
or
OMRON type MY4 220/240ACS in DIN socket type PYF14AE also available from Farnell Components, stock codes 186-508 (relay) and 134-0953 (socket). Optional retaining clips 103-923 (2 off required)
Caution: Use of alternative relay may require pin number changes.
In the above schematic:
Relay contact 1 determines pump live supply from either the boiler in CH mode, or a direct Live feed in HD mode.
Relay contact 2 inhibits boiler SwL supply to prevent boiler firing in HD mode.
Relay contact 3 opens DHW zone valve in HD mode.
Relay contact 4 is not used but allows future expansion to full CH HD if bypass radiator is insufficient.
© A.J.Cooper June 2021

## Solar S-Plan HD bypass Resol
S-Plan (2-Zone) Fully Pumped Wiring Scheme with Solar System, Resol Solar Controller with Bypass Heat Dump
Use this version ONLY if a single radiator is permanently connected to the boiler pump circuit as a bypass e.g. bathroom radiator
[5 empty] | HW |  | CH |  | HW |  | CH
[5 empty] | OFF |  | OFF |  | ON |  | ON |  |  |  |  | COM | ON | OFF | [16 empty] | S1 |  |  |  | S2 |  |  |  | S3 |  |  |  | S4
| Horstmann |  | N | L | 1 |  | 2 |  | 3 |  | 4 |  |  |  |  | C | 1 | 2 | Cylinder Stat | [9 empty] | Resol BS3 / BS4 | [5 empty] | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8
| C27 controller | [17 empty] | Honeywell L641A | [9 empty] | PT1000 sensor connections
[23 empty] | OFF | ON |  | COM | [8 empty] | Collector |  |  |  | Cyl lower |  |  |  | Cyl top |  |  |  | Return
[20 empty] | Danfoss TP5000 |  |  | NC | NO |  | COM | [20 empty] | (optional)
Room stat
4PCO relay - ON with Controller R2 ('Heat Dump' mode)
[30 empty] | C1 9 | NO1 5 | NC1 1 | C2 10 | NO2 6 |  | NC2 2 |  | C3 11 |  | NO3 7 |  | NC3 3 |  | C4 12 |  | NO4 8 |  | NC4 4 |  | Coil 13 |  | Coil 14
230Vac feed from | [13 empty] | N/C | [20 empty] | Earth |  | Earth |  | Earth | [5 empty] | N |  | R1 |  | N |  | L
DP Sw/Fused |  | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 | 9 | 10 | Connection Terminal Box |  |  | N | L | SwL |  | PL | PN | N |  | L |  |  |  |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20
spur with 3A fuse | [6 empty] | 3
[24 empty] | * Boiler |  |  |  | Boiler Pump | [12 empty] | N |  | R2
Resol BS3 / BS4 Controller
[12 empty] | Bl |  | Br |  | Or | Gy |  |  | Bl | Br | Or | Gy |  | 2 off 2-port Zone Valves | [19 empty] | N |  | L
e.g. Horstmann Z222XL
[13 empty] | ZV Central Heating | [7 empty] | ZV DHW |  |  |  | or Honeywell V4043H | [19 empty] | Solar Pump
* For boilers without a PL terminal there will be no connection between Boiler 'PL' and relay 'NC1'. In this case simply link Relay terminal 'NC1' to Relay terminal 'C2'.
Warning: Please read guidance notes accompanying this schematic before use
Suggested relays:
Finder type 5534-8230-0040 in DIN socket type 94.74SMA available from Farnell Components, stock codes 116-9224 (relay) and 913-7653 (DIN relay socket)
or
OMRON type MY4 220/240ACS in DIN socket type PYF14AE also available from Farnell Components, stock codes 186-508 (relay) and 134-0953 (socket). Optional retaining clips 103-923 (2 off required)
Caution: Use of alternative relay may require pin number changes.
In the above schematic:
Relay contact 1 determines pump live supply from either the boiler in CH mode, or a direct Live feed in HD mode.
Relay contact 2 inhibits boiler SwL supply to prevent boiler firing in HD mode.
Relay contact 3 opens DHW zone valve in HD mode.
Relay contact 4 is not used but allows future expansion to full CH HD if bypass radiator is insufficient. | [43 empty] | © A.J.Cooper June 2008

## Solar S-Plan HD to CH Sorel
S-Plan (2-Zone) Fully Pumped Wiring Scheme with Solar System, Sorel Solar Controller with Full Radiator Heat Dump
Use this version to dump excess heat into the entire central heating radiator circuit
[5 empty] | HW |  | CH |  | HW |  | CH
[5 empty] | OFF |  | OFF |  | ON |  | ON |  |  |  |  | COM | ON | OFF | [17 empty] | S3 |  |  | S2 |  |  |  | S1
| Horstmann |  | N | L | 1 |  | 2 |  | 3 |  | 4 |  |  |  |  | C | 1 | 2 | Cylinder Stat | [10 empty] | Sorel TDC2 / TDC3
| C27 controller | [17 empty] | Honeywell L641A | [10 empty] | PT1000 sensor connections
[23 empty] | OFF | ON |  | COM | [9 empty] | Cyl top |  |  | Cyl lower |  |  |  | Collector
[20 empty] | Danfoss TP5000 |  |  | NC | NO |  | COM
Room stat
4PCO relay - ON with Controller R2 ('Heat Dump' mode)
[29 empty] | C1 9 |  | NO1 5 | NC1 1 | C2 10 | NO2 6 | NC2 2 |  | C3 11 | NO3 7 |  | NC3 3 |  | C4 12 |  | NO4 8 |  | NC4 4 |  | Coil 13 |  | Coil 14
230Vac feed from | [13 empty] | N/C
DP Sw/Fused |  | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 | 9 | 10 | Connection Terminal Box |  |  | N | L | SwL |  | PL | PN | N | L | [9 empty] | R2 |  | N |  | L |  | N |  | R1 |  | N
spur with 3A fuse | [6 empty] | 3
[24 empty] | * Boiler |  |  |  | Boiler Pump
Sorel TDC2/3
Controller
[12 empty] | Bl |  | Br |  | Or | Gy |  |  | Bl | Br | Or | Gy |  | 2 off 2-port Zone Valves | [21 empty] | L |  | N
e.g. Horstmann Z222XL
[13 empty] | ZV Central Heating | [7 empty] | ZV DHW |  |  |  | or Honeywell V4043H | [21 empty] | Solar Pump
* For boilers without a PL terminal there will be no connection between Boiler 'PL' and relay 'NC1'. In this case simply link Relay terminal 'NC1' to Relay terminal 'C2'.
Warning: Please read guidance notes accompanying this schematic before use
Suggested relays:
Finder type 5534-8230-0040 in DIN socket type 94.74SMA available from Farnell Components, stock codes 116-9224 (relay) and 913-7653 (DIN relay socket)
or
OMRON type MY4 220/240ACS in DIN socket type PYF14AE also available from Farnell Components, stock codes 186-508 (relay) and 134-0953 (socket). Optional retaining clips 103-923 (2 off required)
Caution: Use of alternative relay may require pin number changes.
In the above schematic:
Relay contact 1 determines pump live supply from either the boiler in CH mode, or a direct Live feed in HD mode.
Relay contact 2 inhibits boiler SwL supply to prevent boiler firing in HD mode.
Relay contact 3 opens DHW zone valve in HD mode.
Relay contact 4 opens CH zone valve in HD mode. | [41 empty] | © A.J.Cooper June 2021

## Solar S-Plan HD to CH Resol
S-Plan (2-Zone) Fully Pumped Wiring Scheme with Solar System, Resol Solar Controller with Full Radiator Heat Dump
Use this version to dump excess heat into the entire central heating radiator circuit
[5 empty] | HW |  | CH |  | HW |  | CH
[5 empty] | OFF |  | OFF |  | ON |  | ON |  |  |  |  | COM | ON | OFF | [16 empty] | S1 |  |  |  | S2 |  |  |  | S3 |  |  |  | S4
| Horstmann |  | N | L | 1 |  | 2 |  | 3 |  | 4 |  |  |  |  | C | 1 | 2 | Cylinder Stat | [9 empty] | Resol BS3 / BS4 | [5 empty] | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8
| C27 controller | [17 empty] | Honeywell L641A | [9 empty] | PT1000 sensor connections
[23 empty] | OFF | ON |  | COM | [8 empty] | Collector |  |  |  | Cyl lower |  |  |  | Cyl top |  |  |  | Return
[20 empty] | Danfoss TP5000 |  |  | NC | NO |  | COM | [20 empty] | (optional)
Room stat
4PCO relay - ON with Controller R2 ('Heat Dump' mode)
[30 empty] | C1 9 | NO1 5 | NC1 1 | C2 10 | NO2 6 |  | NC2 2 |  | C3 11 |  | NO3 7 |  | NC3 3 |  | C4 12 |  | NO4 8 |  | NC4 4 |  | Coil 13 |  | Coil 14
230Vac feed from | [13 empty] | N/C | [20 empty] | Earth |  | Earth |  | Earth | [5 empty] | N |  | R1 |  | N |  | L
DP Sw/Fused |  | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 | 9 | 10 | Connection Terminal Box |  |  | N | L | SwL |  | PL | PN | N |  | L |  |  |  |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20
spur with 3A fuse | [6 empty] | 3
[24 empty] | * Boiler |  |  |  | Boiler Pump | [12 empty] | N |  | R2
Resol BS3 / BS4 Controller
[12 empty] | Bl |  | Br |  | Or | Gy |  |  | Bl | Br | Or | Gy |  | 2 off 2-port Zone Valves | [19 empty] | N |  | L
e.g. Horstmann Z222XL
[13 empty] | ZV Central Heating | [7 empty] | ZV DHW |  |  |  | or Honeywell V4043H | [19 empty] | Solar Pump
* For boilers without a PL terminal there will be no connection between Boiler 'PL' and relay 'NC1'. In this case simply link Relay terminal 'NC1' to Relay terminal 'C2'.
Warning: Please read guidance notes accompanying this schematic before use
Suggested relays:
Finder type 5534-8230-0040 in DIN socket type 94.74SMA available from Farnell Components, stock codes 116-9224 (relay) and 913-7653 (DIN relay socket)
or
OMRON type MY4 220/240ACS in DIN socket type PYF14AE also available from Farnell Components, stock codes 186-508 (relay) and 134-0953 (socket). Optional retaining clips 103-923 (2 off required)
Caution: Use of alternative relay may require pin number changes.
In the above schematic:
Relay contact 1 determines pump live supply from either the boiler in CH mode, or a direct Live feed in HD mode.
Relay contact 2 inhibits boiler SwL supply to prevent boiler firing in HD mode.
Relay contact 3 opens DHW zone valve in HD mode.
Relay contact 4 opens CH zone valve in HD mode.
© A.J.Cooper June 2008

## Standard S-Plan
Standard S-Plan (2-Zone) Fully Pumped Wiring Scheme
[7 empty] | HW |  | CH |  | HW |  | CH
[7 empty] | OFF |  | OFF |  | ON |  | ON |  |  |  | COM |  | ON |  | OFF
| Horstmann |  |  | N | L |  | 1 |  | 2 |  | 3 |  | 4 |  |  |  | C |  | 1 |  | 2 |  | Cylinder Stat
| C27 controller | [21 empty] | Honeywell L641A
[23 empty] | OFF |  | ON | COM
[23 empty] | NC |  | NO | COM | Danfoss TP5000
Room Stat
Heating
[14 empty] | N/C | [13 empty] | Pump
230Vac feed from |  | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 | 8 | 9 | 10 |  |  |  | N |  | L |  | SwL | PL | PN | N | L
DP Sw/Fused | [6 empty] | 3
spur with 3A fuse | [24 empty] | Boiler
* Terminal 9 connection only required when pump is remote from boiler.
For boilers without 'PL' terminal, connect Pump 'L' direct to terminal 10.
[8 empty] | Bl |  | Br |  | Or |  | Gy |  |  |  | Bl |  | Br |  | Or |  | Gy |  | 2 off 2-port Zone Valves
Horstmann Z222XL or
[9 empty] | ZV Central Heating | [10 empty] | ZV DHW | [5 empty] | Honeywell V4043H
|  |  | Warning: Please read guidance notes accompanying this schematic before use | [24 empty] | © A.J.Cooper June 2008